## KRIEGER SPECIALTY PRODUCTS

### 4880 Gregg Road

#### Pico Rivera, CA  90660

Tel:  562-695-0645

Fax:  562-692-0146

SECTION 08342

RADIO FREQUENCY SHIELDED DOOR ASSEMBLY

# PART 1    	GENERAL

  - SECTION INCLUDES

- This section includes steel RF-Tight Doors and frames for facilities designed to contain radio frequency (RF) energy generated from electronic equipment, and/or shield susceptible equipment from electromagnetic interference.

- KriegerShield door assemblies are ideal for high profile interior applications requiring uncompromised quality, design performance; Research and Development laboratories; computer rooms, healthcare facilities, communication centers, boardrooms and military installations or wherever TEMPEST or SCIF standards are a requirement.

1.02	SUBMITTALS

- Submit shop drawings for the fabrication and installation of steel radio frequency shielded doors and frames, as required to supplement manufacturers data and showing location by door numbers. Include details of each frame type, elevations of door design, conditions of anchoring, and dimensional elevations.

  - QUALITY ASSURANCE

A.	Custom Specification: Conform where applicable to "Guide Specifications For Hollow Metal Doors and Frames", NAAMM Standard HMMA 860-87, except as modified herein. Provide letter of certification that manufacturer is a member of NAAMM and/or conforms to these standards.

1.03	SHIELDING EFFECTIVENESS

A.	KriegerShield doors attenuate at least 60 dB of electric field and plane wave energy from 1 kHz through 18 GHz.  Laboratory tested and field verified per NSA 65-6 and MIL-STD-285.

1.04 DELIVERY, STORAGE, AND HANDLING

A. 	All doors and frames shall be fully crated in wood crates and palletized by door manufacturer for handing by forklift to prevent freight damage.

PART 2 	PRODUCTS

2.01	MANUFACTURERS

A.	Acceptable manufacturer:  Krieger Specialty Products, 4880 Gregg Road, Pico Rivera CA 90660; Telephone 562-695-0645, FAX 562-692-0146.

B.	Substitutions:  Not permitted.

C.	Unless otherwise specified for an individual product or material, supply all products specified in this section from the same manufacturer.

  - MATERIALS

A. Doors.

- Exterior radio frequency shielded doors shall be as manufactured by Krieger Specialty Products Co. or approved equal prior to bid.

2. 	Door material shall be 16 gauge stainless steel.  Doors shall be flush construction with provision for contact of RF Gasket.

- All hardware reinforcements to be in conformance to HMMA standards.

4.	UL fire-rated up to and including 3 hours as required by plans and specifications.

B. Frames.

- Exterior frames shall be RF-Tight as manufactured by Krieger Specialty Products Co. or approved equal prior to bid.

2. 	Frame material shall be 14 gauge galvanized G60 steel, profiles as detailed on

Architectural drawings. Profiles and anchors shall be custom fabricated to suit wall conditions and to provide adequate anchoring.  Frames to have continuous contact flange to interface with RF Shielding material on walls and floor.

3.	Corner joint of frames are to be continuous welded and ground smooth.

C.	RF Gasketing.

1.	The frame shall be factory mounted with a formed stainless steel gasket retainer that is conductive with the frame.

2.	KriegerShield assembly shall be provided with a factory installed RF-tight monel wire mesh foam core gasket enhanced with flexible, non-woven metallized fabric.

D. 	Hardware and hardware preparation.

1.	Frames shall have factory-provided with radial bearing cam-lift hinges.

- Latch and locksets, panic devices, security and power operating hardware are options.

3.	Balance of hardware shall be provided by others.  Door manufacturer will provide all necessary cutouts and reinforcement for mortised hardware; and all necessary reinforcements for surface applied hardware, in accordance with approved hardware schedule and HMMA standards.

## E. 	Finish

- Doors and Frames shall be factory primed with rust inhibiting, environmentally safe primer in accordance with HMMA standards.  Prime shall cover all surfaces, except RF contact points without runs, smears or bare spots.

PART 3 	EXECUTION

3.01 PREPARATION

- Inspect wall framing before application to assure opening to receive frames are properly framed, reinforced and there is provision for RF interface.

- Inspect all doors and frames for freight or jobsite damage, and review cutouts for conformance to hardware schedule.

3.02 INSTALLATION

A.	Install frames per manufacturer's printed instructions.  Securely attach to wall framing system.  Frames to be installed square and plumb.

B.	Provide any necessary additional reinforcing to insure a rigid and permanent installation.

C.	Hang doors, install hardware and adjust for smooth operation without binding or sticking.

D.	Remove hardware for painting and re-install after painting is complete.

- Allow proper clearances in accordance with manufacturer's printed instructions.

END OF SECTION